## Feuille1
Fill in the red values only
Turbine output in Kwatt | 1.3926
Number of Nozzle | 1
Radius in metre | 0.0040243
Radius in milimeter | 4.0243
Diameter nozzle(s) en mm | 8.0486
Totale area in m2 | 5.0852e-05
Head in metres or pressure gauge x10 | 80
Head – Head loss m | 78.8629
Speed of water m/s | 39.3296
Pipe efficiency % | 98.5787
Rated flow l/s | 2
Flow m3/s | 0.002
Internal pipe diameter in mm | 70
Pipe diameter m | 0.07
Pipe radius m | 0.035
Pipe area m² | 0.0038465
Pipe Lenght in metres | 250
Average speed of water m/s | 0.51995
Reynolds Number | 31926.2223
Head loss coefficient | 0.023098
Head Loss m | 1.1371